Resilient-seated gate valve to EN 1074 
with DIN-DVGW type approval test certificate
Shut-off valve for drinking and service water up to 50° C
DN 40 - 300, PN 10 - 16
Face-to-face length DIN EN 558-1, basic series 15 (DIN 3202, F5)

Boltless, self-sealing cover connection;
Rubber-coated shut-off wedge with sliding caps to reduce wear and tear and operation torques, which increases the service life;
Significantly lower actuation torques than EN 1072-2 requirement
Maintenance-free and corrosion-resistant stem sealing;
O rings in brass sleeve;
With continuous internal pipe bottom;
Tightness to DIN EN 12,266-1, leakage rate A;
Also suitable for vacuum up to 90%;
Flange connection dimensions to EN 1092-2;
All parts in touch with the fluid to KTW and DVGW Code of Practice W270 (no build-up of harmful bacteria);
Body, cover and wedge made of cast iron EN-JS 1030 (GGG-40);
Wedge EPDM rubber coated on all sides;
Stem made of stainless steel grade 1.4057;

Corrosion protection
Inside and outside epoxy coated in GSK type “heavy-duty corrosion protection” to 
DIN 30 677-2, coating thickness >250 µm, colour: RAL 5005 blue

VAG BETA® 200 Gate Valve or equivalent	

Manufacturer:	VAG GmbH
		Carl-Reuther-Str. 1	
		68305 Mannheim
		Germany
		www.vag-group.com

Varieties:
- with handwheel
- with stem square cap
- with extension spindle
- TELEMAX® stem extension, lockable by DVE sealing and locking unit as protection against dirt
- with surface box
- with carrier plate
- with SERIO®plus position indicator

Quantity ........    €/piece ........    €/item .......