Author: VAG-Group
Last saved by: Thomas Kunzmann
Category: Salestext

Resilient-seated gate valve to EN 1074
with DIN-DVGW type approval test certificate
Shut-off valve for drinking and service water up to 50° C
DN 80 - 300, PN 16
with socket connection in accordance with DIN 28603 on one side and BAIO^® spigot end connection on the other side

With double-function socket on one side for direct internal and external bayonet connection with BAIO^®plus System parts;
Tension-free installation due to an inclination of up to +/- 3 degrees;
Socket form for sealing ring to DIN 28 603;
Variable application suitable for ductile cast-iron and plastic pipes by simple replacement of the seals;
Boltless, pressure supported cover sealing connection;
Rubber-coated shut-off wedge with sliding caps to reduce wear and tear and operation torques, which increases the service life;
Maintenance-free and corrosion-resistant stem sealing;
O rings in brass bush;
With continuous internal pipe bottom;
Tightness to DIN EN 12 266-1, leakage rate A;
All parts in touch with the fluid to KTW and DVGW Code of Practice W270 (no build-up of harmful bacteria);
Body, cover and wedge made of ductile cast iron EN-JS 1030 (GGG-40);
Wedge EPDM rubber coated on all sides;
Stem made of stainless steel grade 431;

Corrosion protection:
Inside and outside epoxy coated in GSK type “heavy-duty corrosion protection” to DIN 30 677-2, coating thickness >250 µm, colour: RAL 5005 blue

VAG BETA^® 200 Gate Valve MU/SP or equivalent	

Manufacturer	VAG GmbH
		Carl-Reuther-Str. 1
		68305 Mannheim
		Germany
		www.vag-group.com

Varieties:
- with TYTON sealing rings
- with GKS sealing rings
- with handwheel
- with stem square cap
- with extension spindle
- with TELEMAX^® stem extension, lockable by DVE sealing and locking unit as protection against dirt
- with surface box
- with carrier plate
_- with SERIO^®plus position indicator

Quantity ........    €/piece ........    €/item .......