Resilient-seated gate valve to EN 1074
Shut-off valve for sea water up to 50° C
DN 40 - 300, PN 10 - 16
Face-to-face length DIN EN 558-1, basic series 14 (DIN 3202, F4)

Rubber-coated shut-off wedge with sliding caps to reduce wear and tear and operation torques, which increases the service life;
Maintenance-free and corrosion-resistant extended stem seal with triple O ring sealing located in the bush;
With flat bottom;
Tightness to DIN EN 12 266-1, leakage rate A;
Also suitable for vacuum up to 90%;
Flange connection dimensions to EN 1092-2;
Body, cover and wedge made of ductile cast iron EN-JS 1030 (GGG-40);
Wedge EPDM rubber coated on all sides;
Stem made of seawater resistant stainless steel AISI 318 (Duplex 1.4462)
Stem nut made of zinc-free bronze

Corrosion protection:
Inside and outside epoxy coated in GSK type “heavy-duty corrosion protection” to 
DIN 30 677-2, coating thickness >250 µm, colour: RAL 5005 blue

VAG EKO®plus Gate Valve – sea water or equivalent

Manufacturer:	VAG GmbH
		Carl-Reuther-Str. 1	
		68305 Mannheim
		Germany
		www.vag-group.com

Varieties:
- with handwheel
- with stem square cap
- with extension spindle
- with TELEMAX® stem extension, lockable by DVE sealing and locking unit as protection against dirt
- with surface box
- with support plate
- with SERIO®plus position indicator
- with electric actuator 
- with pneumatic actuator

Quantity ........    €/piece ........    €/item .......