Underground hydrant with single shut-off 
Type A to EN 1074-6 and EN 14339
DIN-DVGW registered for drinking water
DN 80, PN 16

Double draining system with two independent drain ports with pressure water protection – no remaining water after closing of the Hydrant;
With integrated safety interlock of the main valve assembly;
Self-closing claw cover (continuously adjustable to open position);
Claw with retaining lugs; integrated orifice protection;
Enclosed, backlash-free stem bearing;
Maintenance-free stem seal with triple O ring seal in a brass bushing;
One-piece jacket;
Integrated multi-functional seal at the connection flange;
Flange connection dimensions to EN 1092-2;
All parts in touch with the fluid to KTW and DVGW Code of Practice W270 (no build-up of harmful bacteria);
Jacket, cap and claw made of ductile cast iron;
Valve cone made of ductile cast iron fully vulcanised with EPDM;
Stem made of stainless steel grade 420;
All bolts made of stainless steel grade 304;
Pressure pipe and connecting pins made of stainless steel grade 304;
Stem nut and valve seat bushing made of brass

Corrosion protection:
Inside and outside epoxy coated in GSK type “heavy-duty corrosion protection” to 
DIN 30 677-2, coating thickness >250 µm, colour: RAL 5005 blue

VAG HYDRUS® G1 Underground Hydrant, Type A or equivalent	

Cover depth: 0.75 m, 1.00 m, 1.25 m or 1.50 m

Manufacturer:	VAG GmbH
		Carl-Reuther-Str. 1	
		68305 Mannheim
		Germany
		www.vag-group.com

Quantity ........    €/piece ........    €/item .......